## Slide 1
Design And Calculation Of Central Air Conditioning system (using E20-II Carrier Software )
civil And architecture
engineering building
Ahmed Fawzy Zaki Mohammed
Elsayed Mohammed Abdel Shafi
Kareem El-Sayed Sheta Salem
Mohammed Abd allah Morade
Mohammed Abd El-Azim Mahmoud Elshamndy
Mohammed Hamdy khalifa
Mohammed Galal Abd El-Hakim Azab
Mohammed Shabaan Ibrahim Morsy
Mahmoud Eid Mohammed Eid
Mahmoud Mohammed Rashad
Marwa Sabry El-gendey
Mostofa Fatouh Fangary
Nadia Mohammed Attia
Naglaa Hamdy Eid Abd Rabbou
Reda Rezk Gommaa
Said Ali Mousa Solyman
Shaimaa Ali Ahmed Ahmed
Shaimaa Mohammed Abd Alaziz

## Slide 2
Project Tasks
Step (1) Draw or study the civil and architecture building drawing sheet.
Step (2) Search for the thermal properties of the building
Step (3) Determine the compass direction (North – South. etc.)
Step (4) Calculation the usage of the different places as well as numbers of people occupancy these places.
Step (5): Determine the internal and external design conditions.
Step (6): Estimate the thermal loads.
Step (7): calculation the rate of air flow for each zone.
Step (8): Design duct for the control A/C such, supply air lines and return air lines.
Step (9): Determine the rectangular air ducts.
Calculation the friction losses through the outlines to select air supply.
Determine the outlet air capacities for each zone.
Estimate the air ducts losses.
Calculation the cooling coils capacities to choose the cooling unit.
The bill.

## Slide 3
Introduction
Air conditioning can be defined as the control of temperature, humidity, cleanliness, odor and air circulation as required by the occupants of the space.
The factors that influence comfort, in there order of importance are:
Temperature, humidity, air motion and the quality of the air with regard to odor, dust and bacteria.
  Classification of Air Conditioning Systems
  Air conditioning system can be classified into two main categories as follows:
According to their function (comfort and processing air conditioning system).
According to their construction and operating characteristics
Classification of Air Conditioning Apparatus
1. Unitary equipment: Unitary equipment can be divided into:-
A- Window type.
B- Split type.
2. Central system components:
Most large buildings, however, have their own central equipment plant and the choice of equipment depends on:
1. Required capacity and type of usage.
2. Cost and kinds of available energy.
3. Location of the equipment room.
4. Type of air distribution system.
5. Owning and operating costs.

## Slide 4
Building in the studying building for architecture and civil engineering which is located in east air shows inside the faculty of engineering (material) and has length of (69.78) m, width of (37) m, height of (35.50) m and area of (2057.86) m2.
Building description
The building consist of five floor in addition to the first floor. Which consist of two amphitheater and fear hall and each floor has 20 room.
The bottoming floor includes a computer hall and one fear hall , Two amphitheater, and room and the third floor is consist of twenty room which includes two drawing hall.
The Building Direction
In the north: District separate between this building and administration building.
In the south : District separate between this building and the shops.
In the east: Garden
In the west : AL Shahed Mustafa Hafez street
Building Design Condition
Latitude = 30
The dry outlet temperature = 37.7 o C from Carrier
The wet outlet temperature = 26.7 o C
The dry inlet temperature = 24 o C
The relative humidity = 47%

## Slide 5
LOAD ESTIMATING

## Slide 6
Calculation of
Heat Transfer Through
Wall due to
Temperature Difference
Load Calculation
due to Sun
Load Calculation due to
Ventilation
Load Calculation
due to Person
Load Calculation
duo to Light
Load Calculation due to
Infiltration
Load Calculation
due to Equipment
Steps of Load Estimation

## Slide 7
Cooling Load Calculation of the Computer Room:
Height wall:
h =5.6 m
Windows :
W1 = 1.2*0.8 m2
W2 = 0.6*0.8 m2
Door :
D1=1.2*1 m2
Area Calculation:
∑area | Area | Item
2.88 | 2(1.2*0.8)+2(.6*0.8) | Glass W
2.4 | 2(1.2*1) | Door E
8.4 53 38.52 54.52 | (1.5*5.6) (10.25*5.6)-(2.4) (6.88*5.6) (10.25*5.6)-(2.88) | Wall N E S W
70.52 | (10.25*6.88) | Ceiling
Calculation of Heat Transfer Through Wall due to Temperature Difference :
Q = ∑A×U×∆T
External wall
Uw =1/hi+1/ho+∑∂/K i
Internal wall
Uw =1/hi+1/hi+∑∂/K i

## Slide 8
From Table Determining the Coefficient of heat
transfer the Windows and doors
Windows:
Single Glass = 6.08 (W/m .k)
Door :
Solid Wood Door Thickness (50mm) = 2.47 (W/m .k)
Calculation of heat transfer through wall due to temperature difference
Load Calculation due to Sun:
Qsun = ∑AUΔTsun + ∑A(w/m2)glass × S.C
From Table Determining the heat transfer from the sun to wall due to temperature difference.
From Table Determining the Heat transfer through glass.
From Table Determining the shadow coefficient

## Slide 9
Load Calculation due to Equipment:
From Table Determining the heat gain due to equipment.
QE = ∑Q
QE = (18×200)+(1×150) = 3750 (W)
Load Calculation duo to Light:
QL = n×(W/lamp)×1.25
Lamp length 120 cm = 40 (w/lamp)
Lamp length 60 cm = 20 (w/lamp)
QL = 70.52×40 =2820 W

## Slide 10
Load Calculation due to Person:
QP = n × (q/person)
From Table Determining the heat gain due to persons

## Slide 11
Ventilation Load Calculation :
Q v = n [(L/S/person) ×10-3] × (1/Vo) [(ho-hi) ×103
Qvs= 20 × 7× 10-3× (1/0.9) × (68.4-26) × 103 = 5936 (W)
Q vl= 20 × 7× 10-3× (1/0.9) × (68.4-53) × 103 = 2156 (W)

## Slide 12
Infiltration Load Calculation :
Qis = ∑L (l/s) /m ×10-3) × (1/vo) × (cp (to - ti) × 103)
∑L = 2 (1.2+0.8) × 2 + 2 (0.8+0.6) × 2 = 13.6 ( m2)
∑L = 2 (1.2+1) 2 = 8.8 m2
Qis = (13.6 × 0.82 + 8.8 × 2.8) 10-3 (1/0.9) (1.005 (41-26) ×103) = 599.5 (W)
Qil = ∑L (l/s) /m ×10-3) × (1/vo) × (ho – hi) 103
Qil = ((13.6×0.82) + (8.8×2.8) 10-3 (1/0.9) (64.4-53) 103 = 453 (W)
Neglect infiltration load calculation

## Slide 13
Summation sensible and latent load
Qt | Ql | Qs | Item
3983.84 |  | 3983.84 | Qt
3889.2 |  | 3889.2 | Qsun
3750 |  | 3750 | Qeq
2820 |  | 2820 | Qlit
2340 | 900 | 1440 | Qp
8092 | 2156 | 5936 | Qv
24.875 kW | 3.056 kW | 21.819 kW | ∑Q

## Slide 14
Block Load Program

## Slide 15
:Zone nameRoom
STEP 1: Define Weather Data
Step 2 : Enter zone data ……(screen 1)

## Slide 16
2 : Enter zone data …..(screen 2 of 3 )Step
Step: 2 Enter zone data …….. (screen 3 of 3)

## Slide 17: Step 3 : define HVAC system data …(Screen 1 of 2)
Step 4: calculation load

## Slide 18
Step 3: define HVAC data ……(screen 1 of 2)
Step 4 : calculate loads

## Slide 19
System sizing summary

## Slide 20
[E20-II] HVAC PROGRAM
DESIGN
E20-II is a family of HVAC system engineering
design and analysis programs developed by
Carrier Corporation for use on microcomputers.
These takes include cooling and heating load estimating, duct system design. Piping design.

## Slide 21
The E20-II family of programs consists of two basic elements:
The E20-II configuration program
The E20-II HVAC Design Programs

## Slide 22
Block Load Program
Block load is computer program which calculates cooling and heating loads for buildings.It also providesdata required to size and select cooling and heating equipment.

## Slide 23
To calculate loads and size equipment, a simple 4-step procedure is required. Block load is structured to guide the user guide and easily through these steps
Step 1 Defining Weather Data
Step 2 Entering Zone data
Step 3 Defining HVAC System Data
Step 4 Calculating loads

## Slide 24
Air Duct Design

## Slide 25: 1-Introduction
Air distribution systems transmit the air from the air conditioning equipment to the space to be conditioned, and then back to the equipment. The simplest combination of fans, duct and outlets usually results in the best system.

## Slide 26: 2- Types of Air Duct
A-Supply duct:
  conditioned air is supplied to the conditioned space.
B-Return duct:
  spaces air is returned to the fan room
C-Outdoor air duct :
  outdoor air is transported to the air handling unit, to the fan room.
D-Exhausted duct :
  spaces air or contaminated air is exhausted from the space

## Slide 27: 3- Duct system
A- loop perimeter :
  In a loop perimeter, the supply duct is installed in a continuous, closed loop around the perimeter of the building.

## Slide 28: B- Radial perimeter
  In a radial perimeter system, the supply air is delivered from a central plenum in separate ducts running from the plenum to each outlet.

## Slide 29: C- Extended plenum
  An extended plenum system has a rectangular plenum extended from one or both sides of the heating or cooling source

## Slide 30: D-Overhead trunk
  In an overhead trunk system the main plenum or trunk is extended in a false ceiling usually down a center hall

## Slide 31: E-Overhead radial
  The overhead radial system does not have an extended plenum. The supply air flows directly from the central plenum through duct located in a (false) hall ceiling.

## Slide 32: 4- The steps of air duct design
A- Determining the quantity of air required for each room by using this relation :
  Q = 1.232 V ∆T
  Q: Thermal load (summation of sensible heat and latent heat) (kW)
  V: Volume flow rate of supply (cms)
  ∆T: temperature difference between the indoor temperature and supply air temperature

## Slide 33
B-Determining the number of diffusers and its distribution through each room according to:
  1- Area of the room .
  2-The quantity of air .
  3-The recommended noise level .
C- Select duct system suitable for our design .

## Slide 34
D- According to distribution we can determine the quantity of air for each duct

## Slide 35
E- Duct sizing: we can use one of the following methods :
  1- Equal friction method with maximum velocity .
  2- Static regain method .
  3- Constant velocity method .
  4- T method .

## Slide 36
By using equal friction method with maximum velocity we can determine the
Friction equivalent diameter.
Diameter
line
Velocity
line
Friction losses chart

## Slide 37
F- By using equivalent diameter chart, we ca determine dimension of rectangular duct.

## Slide 38
g- Calculation of the fan power by determining the following :
  a- volume of air required to supply.
  b- The pressure drop (fittings, grilles, filters, coils...) in index run .
  By using this relation we can determine the amount of the fan power P= Δp* V/ ή
    Δp: The pressure drop
    V : Volume flow rate of supply
    ή :efficiency of fan

## Slide 39: Air duct design by Carrier software(E20-II)

## Slide 40: Step (1)

## Slide 41: Step (2)

## Slide 42: Step (3)

## Slide 43: Step (4)

## Slide 44: Step (5)

## Slide 45: Step (6)

## Slide 46: Step (7)

## Slide 47: Step (8)

## Slide 48: Step (9)

## Slide 49: ROOM AIR DISTRIBUTION
This chapter discusses the distribution of conditioned air after it has been transmitted to the room.
Requirements necessary for
A good distribution
Temperature
Air velocity
Air direction

## Slide 50: Temperate
A. Primary Air
Primary Air is defined as the conditioned air discharged by the supply outlet plus entrained room air
B. Total Air
Total Air is defined as the mixture of primary air and entrained room air

## Slide 51: AIR DIRECTION
Air motion is desirable and actually necessary.
Fig is a guide to the most desirable air direction for a seated person.

## Slide 52: Outlet Types
Supply opening.
Return opening.
Ceiling diffuser.
Grille.

## Slide 53: Outlet Locations
Low Wall outlets.
High Wall outlets.
Ceiling Diffuse.
Window outlets.
Floor outlet.

## Slide 54: Shapes of Used Ceiling Diffusers

## Slide 55: Shapes of Wall Diffusers

## Slide 56: Selection of outlets
The air flow rate for every room
Size of outlet
Shape of outlet
Noise level
Selection of outlets according to:

## Slide 57
Are used to move air through ducts and to induce air motion in the space .
FANS

## Slide 58: Types of fans
Centrifugal Fans
Axial Fans

## Slide 59
1.Centrifugal Fans
In which the air flows radially through the impeller
It is used in most comfort applications because of its wide range of quiet

## Slide 60
2.Axial Fans
In which the air flows axially through the impeller
are excellent for large air volume applications where higher noise levels are of secondary concern

## Slide 61: Fan selection
To select fan it is necessary to know
the capacity
the efficiency
the size and the weight
The speed and the noise
The cost

## Slide 62: Air Cleaning and Filtration
Filtration can be defined as the process of separating dispersed particles from a dispersing fluid by means of porous media.

## Slide 63: Air Contamination
Dusts
Fumes
Smokes
Mists and Fogs
Vapours and Gases
Organic Particles

## Slide 64: Air Filtration
Types Of Filters:
1- Dry Filters.
2- Wet Filters.
3- Electric Filters.
4- Viscous Filters.
5- Electronic Filters.
6-Centrifugal collectors

## Slide 65: Shapes Of Some Filters
1- Dry Filter.

## Slide 66
2- Electric Filter.

## Slide 67
3- Viscous Filters.

## Slide 68
4-Centrifugal collectors

## Slide 69: A Liquid Chiller is a Central Air Conditioning System

## Slide 70: TYPES OF the SYSTEMS
Direct expansion
All - water
All - air
Air - water
Heat pump

## Slide 71: System Used in Project
Advantages All Air System
All Air System
Multi - Zone
Draw Through Coil
Constant Air Volume & Variable Temperature system
Roof – Top
Medium Capacity
Design Simplicity and Operating
Low Primacy Cost
Operating Composure and Maintenance central

## Slide 72: Types of Liquid Chillers
Air Cooled Chillers
Water Cooled Chillers
Evaporative Cooled Chillers
Air cooled chillers are the most commonly used due to convenience of low maintenance.
move the ambient air. However, power usage is
higher, due to the condenser fan motors
(in addition to the compressor motors) which are
required to move the ambient air.
Depending on ambient temperatures, condensing
temperatures of 120° to 140° F are required.
Water cooled chillers require cooling tower, city
water, river water or other source of water to operate.
Lower condensing temperatures provide longer life of compressor
Lower condensing temperatures save energy, approximately 20-25% over air cooled chillers
There are no condenser fan motors, only condenser water pump and cooling tower fan
Highest efficiency, lowest operating costs
Longer equipment life

## Slide 73
Chillers unit used in project
Water Cooled Chiller
Calculation
Selection Chiller
Selection pump

## Slide 74: Water Cooled Chiller
Air handing unit
Evaporative
CONDENSERS
Compressor
Expansion valve
Cooling tower
pump
pump
Air outlet
Air inlet

## Slide 75
Calculation Chiller Plant Design
1-Calculation the cooling load

## Slide 76
2- Calculation the power compressor
3- Calculation the mass flow rate of water to cooling coil

## Slide 77
Selection Chiller
YC W S 0423 S C 50 Y B
YOR WATER SCREW NOMINAL STANDARD REFRIGERANT VOLTAGE TYPE DESIGN
COOLED COMPRESSOR CAPACITY EFFICIENCY R22 CODE START SERIES
Nomenclature

## Slide 78: GUIDE TO SELECTION
Design cooling capacity kW
Entering and leaving chilled water temperatures
Entering and leaving condenser water temperatures
Chilled water flow l/s if one of the temperatures
Condenser water flow l/s if one of the temperatures
Cooler and condenser fouling factors Determine the capacity
Selection Data
5C | Chilled water range
432 kW | Capacity of one unit ( kW)
6 | Number of unit

## Slide 79: UNIT : YCWS 0563SC

## Slide 80: Correction
EVAPORATOR
CONDENSER
Physical Data

## Slide 81
Selection pump
Selection pump Evaporator
The chilled water flow= 21 l/s
Number of pump evaporator = 6
Total chillers water flow = 6 *21 = 126 l/s

## Slide 82
Selection pump Condenser
The chilled water flow= 27 l/s
Number of pump evaporator = 6
Total chillers water flow = 6 *27= 162 l/s

## Slide 84
Introduction
The purpose of this chapter is to discuss the design of control systems for central air conditioning of Civil Architectural engineering building.
First of all, the term (HVAC) means heating, ventilating and air conditioning which covers a wide range of equipment.
control systems

## Slide 85: Aims of Control
1. To regulate the system so that comfortable conditions are maintained in the occupied space.
2. To operate the equipment efficiently.
3. To protect the equipment and the building from damage and the occupants from injury .

## Slide 86: Basic components of control systems
Valves for liquids
Valves for control air
Dampers to restrict the flow of air
Manual pressure regulator for control air
Pressure regulators for working fluids, e.g., steam
Differential-pressure regulators
Velocity sensors
Thermostats
Temperature transmitters
Receiver-controllers
Humidistat
Master and sub master controllers
Reversing relays for control pressure
Pressure selectors
Pneumatic electric switches
Freeze stats

## Slide 87: ENERGY SOURCES FOR CONTROL SYSTEMS
Electric Systems
Electronic Systems
Pneumatic Systems
Hydraulic Systems
Fluidic Systems
Self-Contained System

## Slide 88: PNEUMATIC CONTROL DEVICES
Pneumatic controls are powered by compressed air, usually 102 to 135 kpa which used for operating very large valves or dampers.
Relay-Type Controllers
Bleed-Type Controllers